By BrownS.B. No. 1296

A BILL TO BE ENTITLED

AN ACT

relating to the testing of LP-gas piping systems in school facilities.

BE IT ENACTED BY THE LEGISLATURE OF THE STATE OF TEXAS:

SECTION 1.  Chapter 113, Natural Resources Code, is amended by adding Section 113.054 to read as follows:

Sec. 113.054.  TESTING OF LPG SYSTEMS IN SCHOOL FACILITIES. (a)  At least every two years, before the beginning of the school year, each school shall conduct a leak test on the LPG system in each school facility. The testing may be performed on a two-year cycle under which approximately one-half of the facilities are leak-tested each year. If a school operates one or more school facilities on a year-round calendar, the leak test in each of those facilities shall be conducted and reported not later than July 1 of the year in which the leak test is performed. For the purposes of this section, "school facility" means an entity created in accordance with the laws of the State of Texas and accredited by the Texas Education Agency pursuant to the Texas Education Code, Chapter 39, Subchapter D, but does not include home schools.

(b)  The leak test shall determine whether the LPG system holds at least the pressure as specified in National Fire Protection Association (NFPA) 54, National Fuel Gas Code.

(c)  The leak test shall be conducted in accordance with NFPA 54.

(d)  Within ten calendar days after completion of the leak test, each school shall provide written notice to the school's LPG supplier and to the governing authority of the school facility at which the leak test was conducted. The written notice shall specify the date and result of each leak test and, in the event a leak is detected, the corrective action taken to eliminate the leak. The school shall also provide such written notice to any other LPG supplier used by the school before that supplier delivers LPG to the school.

(e)  The supplier shall maintain a copy of the notice for two years after the date on which the supplier received the notice.

(f)  A supplier shall terminate service to a school facility if:

(1)  the supplier receives official notification from the person conducting the leak test that there is a leak in the facility piping system; or

(2)  the school fails to perform a leak test at the facility as required by this section.

(g)  For purposes of this section, "supplier" means the person selling and delivering the LPG to a school district facility. If more than one person sells and delivers LPG to facilities of a school district, each person is a supplier for purposes of this section.

(h)  If requested by a school, the Railroad Commission shall assist a school in certifying a school district employee to conduct the necessary leak test.

(i)  The Railroad Commission may adopt rules necessary to administer and enforce this section.

(j)  The Railroad Commission shall enforce this section, and is given jurisdiction over schools for the purpose of ensuring compliance with the requirements of this section.

SECTION 2.  Notwithstanding Sec. 113.054, Natural Resources Code, as added by this Act, if a school is not able, before the beginning of the 2000-2001 school year, to conduct the leak tests as required by that section, the school shall conduct the tests as soon as practicable thereafter. In that case, a supplier, as defined by Sec. 113.054, Natural Resources Code, as added by this Act, may not terminate service to a school facility if:

(1)  the school gives written notice to the supplier before the beginning of the 2000-2001 school year that the school is not able to perform the tests before the beginning of the school year; or

(2)  the Railroad Commission orders the supplier not to terminate the service.

SECTION 3.  The importance of this legislation and the crowded condition of the calendars in both houses create an emergency and an imperative public necessity that the constitutional rule requiring bills to be read on three several days in each house be suspended, and this rule is hereby suspended, and that this Act take effect and be in force from and after its passage, and it is so enacted.